## 52.14_K1
T	PVC	XLPE	MIN_LT	MIN_HT
10	1.22	1.15	1.26	1.14
15	1.17	1.12	1.2	1.11
20	1.12	1.08	1.14	1.07
25	1.06	1.04	1.07	1.04
30	1	1	1	1
35	0.94	0.96	0.93	0.96
40	0.87	0.91	0.85	0.92
45	0.79	0.87	0.78	0.88
50	0.71	0.82	0.67	0.84
55	0.61	0.76	0.57	0.8
60	0.5	0.71	0.45	0.75
65	-	0.65	-	0.7
70	-	0.58	-	0.65
75	-	0.5	-	0.6
80	-	0.41	-	0.54
85	-	-	-	0.47
90	-	-	-	0.4
95	-	-	-	0.32

## 52.17_K2
	1	2	3	4	5	6	7	8	9	12	16	20
Bunched in air, on a / surface, embedded or / enclosed.	1	0.8	0.7	0.65	0.6	0.57	0.54	0.52	0.5	0.45	0.41	0.38

Single layer on wall, floor / or unperforated cable tray systems	1	0.85	0.79	0.75	0.73	0.72	0.72	0.71	0.7	0.7	0.7	0.7

Single layer fixed directly / under a wooden ceiling	0.95	0.81	0.72	0.68	0.66	0.64	0.63	0.62	0.61	0.61	0.61	0.61

Single layer on a perforated / horizontal or vertical / cable tray systems	1	0.88	0.82	0.77	0.75	0.73	0.73	0.72	0.72	0.72	0.72	0.72

Single layer on cable ladder systems or cleats etc.,	1	0.87	0.82	0.8	0.8	0.79	0.79	0.78	0.78	0.78	0.78	0.78

## 52.20
C1	C2	C3	C4	C5	C6	C7	C8	C9	C10
Horizontal perforated cable tray systems	Cable touching	31	1	1	0.88	0.82	0.79	0.76	0.73
Horizontal perforated cable tray systems	Cable touching	31	2	1	0.87	0.8	0.77	0.73	0.68
Horizontal perforated cable tray systems	Cable touching	31	3	1	0.86	0.79	0.76	0.71	0.66
Horizontal perforated cable tray systems	Cable touching	31	6	1	0.84	0.77	0.73	0.68	0.64
Horizontal perforated cable tray systems	Cable spaced one cable dia.	31	1	1	1	0.98	0.95	0.91	-
Horizontal perforated cable tray systems	Cable spaced one cable dia.	31	2	1	0.99	0.96	0.92	0.87	-
Horizontal perforated cable tray systems	Cable spaced one cable dia.	31	3	1	0.98	0.95	0.91	0.85	-
Vertical perforated cable tray systems	Cable touching	31	1	1	0.88	0.82	0.78	0.73	0.72
Vertical perforated cable tray systems	Cable touching	31	2	1	0.88	0.81	0.76	0.71	0.7
Vertical perforated cable tray systems	Cable spaced one cable dia.	31	1	1	0.91	0.89	0.88	0.87	-
Vertical perforated cable tray systems	Cable spaced one cable dia.	31	2	1	0.91	0.88	0.87	0.85	-
Horizontal unperforated cable tray systems	Cable touching	31	1	0.97	0.84	0.78	0.75	0.71	0.68
Horizontal unperforated cable tray systems	Cable touching	31	2	0.97	0.83	0.76	0.72	0.68	0.63
Horizontal unperforated cable tray systems	Cable touching	31	3	0.97	0.82	0.75	0.71	0.66	0.61
Horizontal unperforated cable tray systems	Cable touching	31	6	0.97	0.81	0.73	0.69	0.63	0.58
Horizontal cable ladder systems,cleats etc.	Cable touching	32,33,34	1	1	0.87	0.82	0.8	0.79	0.78
Horizontal cable ladder systems,cleats etc.	Cable touching	32,33,34	2	1	0.86	0.8	0.78	0.76	0.73
Horizontal cable ladder systems,cleats etc.	Cable touching	32,33,34	3	1	0.85	0.79	0.76	0.73	0.7
Horizontal cable ladder systems,cleats etc.	Cable touching	32,33,34	6	1	0.84	0.77	0.73	0.68	0.64
Horizontal cable ladder systems,cleats etc.	Cable spaced one cable dia.	32,33,34	1	1	1	1	1	1	-
Horizontal cable ladder systems,cleats etc.	Cable spaced one cable dia.	32,33,34	2	1	0.99	0.98	0.97	0.96	-
Horizontal cable ladder systems,cleats etc.	Cable spaced one cable dia.	32,33,34	3	1	0.98	0.97	0.96	0.93	-

## 52.21
C1	C2	C3	C4	C5	C6	C7

Horizontal perforated cable tray systems	Cable touching	31	1	0.98	0.91	0.87
Horizontal perforated cable tray systems	Cable touching	31	2	0.96	0.87	0.81
Horizontal perforated cable tray systems	Cable touching	31	3	0.95	0.85	0.78
Vertical perforated cable tray systems	Cable touching	31	1	0.96	0.86	-
Vertical perforated cable tray systems	Cable touching	31	2	0.95	0.84	-
cable ladder systems,cleats etc.	Cable touching	32,33,34	1	1	0.97	0.96
cable ladder systems,cleats etc.	Cable touching	32,33,34	2	0.98	0.93	0.89
cable ladder systems,cleats etc.	Cable touching	32,33,34	3	0.97	0.9	0.86
Horizontal perforated cable tray systems	Cables group spaced ≥ 2*De (De = one cable diameter)	31	1	1	0.98	0.96
Horizontal perforated cable tray systems	Cables group spaced ≥ 2*De (De = one cable diameter)	31	2	0.97	0.93	0.89
Horizontal perforated cable tray systems	Cables group spaced ≥ 2*De (De = one cable diameter)	31	3	0.96	0.92	0.86
Vertical perforated cable tray systems	Cables group spaced ≥ 2*De (De = one cable diameter)	31	1	1	0.91	0.89
Vertical perforated cable tray systems	Cables group spaced ≥ 2*De (De = one cable diameter)	31	2	1	0.9	0.86
cable ladder systems,cleats etc.	Cables group spaced ≥ 2*De (De = one cable diameter)	32,33,34	1	1	1.008	1
cable ladder systems,cleats etc.	Cables group spaced ≥ 2*De (De = one cable diameter)	32,33,34	2	0.97	0.95	0.93
cable ladder systems,cleats etc.	Cables group spaced ≥ 2*De (De = one cable diameter)	32,33,34	3	0.96	0.94	0.9

## 52.15
C1	C2	C3
10	1.1	1.07
15	1.05	1.04
20	1	1
25	0.95	0.96
30	0.89	0.93
35	0.84	0.89
40	0.77	0.85
45	0.71	0.8
50	0.63	0.76
55	0.55	0.71
60	0.45	0.65
65	-	0.6
70	-	0.53
75	-	0.46
80	-	0.38

## 52.18
C1	C2	C3	C4	C5	C6
2	0.75	0.8	0.85	0.9	0.9
3	0.65	0.7	0.75	0.8	0.85
4	0.6	0.6	0.7	0.75	0.8
5	0.55	0.55	0.65	0.7	0.8
6	0.5	0.55	0.6	0.7	0.8
7	0.45	0.51	0.59	0.67	0.76
8	0.43	0.48	0.57	0.65	0.75
9	0.41	0.46	0.55	0.63	0.74
12	0.36	0.42	0.51	0.59	0.71
16	0.32	0.38	0.47	0.56	0.38
20	0.29	0.35	0.44	0.53	0.66

## 52.19
Multi-core cables in single-way ducts	2	0.85	0.9	0.95	0.95
Multi-core cables in single-way ducts	3	0.75	0.85	0.9	0.95
Multi-core cables in single-way ducts	4	0.7	0.8	0.85	0.9
Multi-core cables in single-way ducts	5	0.65	0.8	0.85	0.9
Multi-core cables in single-way ducts	6	0.6	0.8	0.8	0.9
Multi-core cables in single-way ducts	7	0.57	0.76	0.8	0.88
Multi-core cables in single-way ducts	8	0.54	0.74	0.78	0.88
Multi-core cables in single-way ducts	9	0.52	0.73	0.77	0.87
Multi-core cables in single-way ducts	10	0.49	0.72	0.76	0.86
Multi-core cables in single-way ducts	11	0.47	0.7	0.75	0.86
Multi-core cables in single-way ducts	12	0.45	0.69	0.74	0.85
Multi-core cables in single-way ducts	13	0.44	0.68	0.73	0.85
Multi-core cables in single-way ducts	14	0.42	0.68	0.72	0.84
Multi-core cables in single-way ducts	15	0.41	0.67	0.72	0.84
Multi-core cables in single-way ducts	16	0.39	0.66	0.71	0.83
Multi-core cables in single-way ducts	17	0.38	0.65	0.7	0.83
Multi-core cables in single-way ducts	18	0.37	0.65	0.7	0.83
Multi-core cables in single-way ducts	19	0.35	0.64	0.69	0.82
Multi-core cables in single-way ducts	20	0.34	0.63	0.68	0.82
Single-core cables in non-magnetic single-way ducts	2	0.8	0.9	0.9	0.95
Single-core cables in non-magnetic single-way ducts	3	0.7	0.8	0.85	0.9
Single-core cables in non-magnetic single-way ducts	4	0.65	0.75	0.8	0.9
Single-core cables in non-magnetic single-way ducts	5	0.6	0.7	0.8	0.9
Single-core cables in non-magnetic single-way ducts	6	0.6	0.7	0.8	0.9
Single-core cables in non-magnetic single-way ducts	7	0.53	0.66	0.76	0.87
Single-core cables in non-magnetic single-way ducts	8	0.5	0.63	0.74	0.87
Single-core cables in non-magnetic single-way ducts	9	0.47	0.61	0.73	0.86
Single-core cables in non-magnetic single-way ducts	10	0.45	0.59	0.72	0.85
Single-core cables in non-magnetic single-way ducts	11	0.43	0.57	0.7	0.85
Single-core cables in non-magnetic single-way ducts	12	0.41	0.56	0.69	0.84
Single-core cables in non-magnetic single-way ducts	13	0.39	0.54	0.68	0.84
Single-core cables in non-magnetic single-way ducts	14	0.37	0.53	0.68	0.83
Single-core cables in non-magnetic single-way ducts	15	0.35	0.52	0.67	0.83
Single-core cables in non-magnetic single-way ducts	16	0.34	0.51	0.66	0.83
Single-core cables in non-magnetic single-way ducts	17	0.33	0.5	0.65	0.82
Single-core cables in non-magnetic single-way ducts	18	0.31	0.49	0.65	0.82
Single-core cables in non-magnetic single-way ducts	19	0.3	0.48	0.64	0.82
Single-core cables in non-magnetic single-way ducts	20	0.29	0.47	0.63	0.81

## 52.16
C1	C2
0.5	1.28
0.7	1.2
1	1.18
1.5	1.1
2	1.05
2.5	1
3	0.96